## User Manual
Solar Aerial Thermography Best Practices Mark Checklist (2024 edition) - User Manual

## Aerial Thermography Checklist
Solar Best Practices Mark Checklist - Aerial Thermography (2024 edition)
http://www.solarbestpractices.com/ |  | Version 02.01.2023 |  |  |  |  | The Solar Best Practices Mark is powered and maintained by SolarPower Europe. www.solarpowereurope.org
The requirements have been developed by SolarPower Europe's Lifecycle Quality workstream.
Contractor details |  |  | Contractor logo
Company name: | [Company name] |  | Insert your logo here |  |  |  | Maximum Score: | 100
Address: | [Address] | [5 empty] | Score needed for compiance: | 80
Website: | [Website] | [5 empty] | [Company name]'s score: | 0
Contact person: | [Contact person] | [5 empty] | [Company name]'s result:
E-Mail: | [E-Mail] | [5 empty] | [Company name] does not meet the eligibility criteria of the Solar Best Practices Mark
Phone: | [Phone]
# | Requirements title and description | Max Score | Self-evaluation |  |  | Your Score | Explanations | Documents for the technical dossier | Calculation (this is not invisible to users)
A | Inspection Requirements | 29 | Fully fulfilled | Partly fulfilled | Not fulfilled | 0 |  |  | Answer (3=fully, 2=party, 1=not fulfilled) | Value
A.1 | Safety training and equipment | 5 |  |  |  | 0 | The Contractor's personnel (including subcontrators, if applicable) has received appropriate safety training and has the necessary safety equipment. | - Copies of safety training documentation - Battery transport procedures - Explanation of procedures for ensuring training and compliance to all employees and subcontractors | 1 | 0%
A.2 | Compliance with local aviation legislations | 6 |  |  |  | 0 | The Contractor ensures that it complies, and that all of its subcontractors comply, at all times with the relevant aviation legislation. | - Licence information for all pilots, or reference to a national body maintaining accreditation for all pilots utilized -Explanation of procedures to ensure compliance for all employees and subcontractors | 1 | 0%
A.3 | Qualification and training personnel | 6 |  |  |  | 0 | The Contractor ensures that the pilots (including subcontractors, if applicable) have appropriate knowledge of the functionality of a PV plant and extensive experience in the field of piloting flight systems. Tick "fully fulfilled" if the pilots hold both, a training certification as flight system operators (UAV or piloted platform) and a valid flight licence issued by the corresponding aviation authorities of each country where the Contractor intends to operate. Tick "partially fulfilled" if only a training certification is in place. | - Certificates or proof of training for all operators of aerial equipment - Certificates or proof of training for all operators of thermographic equipment -Certificates or proof of training for all operators of analysis tools - Explanation of procedures for ensuring uniformity of qualification and training to all employees and subcontractors | 1 | 0%
A.4 | IR Camera & visual photo requirements | 7 |  |  |  | 0 | The Contractor fulfills all camera requirements regarding IEC TS 62446-3 includuing collection of radiometric and visual RGB data or describes deviations of these requirements inside the inspection report. | - Technical specifications of cameras used, including NEDT, minimum abosolute thermal error, integration time - Valid calibration certificates for all thermography equipment utilized | 1 | 0%
A.5 | Recording ambient conditions | 5 |  |  |  | 0 | The Contractor fulfills all requirements for equipment to record ambient condition regarding IEC TS 62446-3 or describes deviations of these requierements inside the inspections report. | -List of ambient measures taken during sample period -Description of any standard deviations from IEC 62446-3 | 1 | 0%
B | Inspection Procedure | 22 | Fully fulfilled | Partly fulfilled | Not fulfilled | 0
B.1 | Flight preparation | 3 |  |  |  | 0 | Integration of requirements into pilots flight preparation. E.g. training, checklists | - Pilots checklists - Document standard site safety requirements to ensure safety for all personell on site | 1 | 0%
B.2 | Environmental conditions | 6 |  |  |  | 0 | Inspection should be performed under environmental conditions specified in IEC TS 62446-3. | - Expected time for inspections for sites of different sizes and allowable variation of meterological conditions during the period of inspections - Procedures for scheduling flights, and explanation of rescheduling charges - if any - in the case of changes in meterological conditions - Documentation in reports of any notable meterological variation during inspections | 1 | 0%
B.3 | Flight requirements | 6 |  |  |  | 0 | Integration of requirements and standards into pilots flight E.g. manual how to fly (angle of flight, max. velocity of the flight platform, taking care of reflections and changing environmental conditions) | - Flight Standards Manual - Descritpion of procedures in place to ensure consistency between all employees and subcontractors | 1 | 0%
B.4 | Thermal camera geometric resolution requirements | 7 |  |  |  | 0 | Check with the client what they hope to achieve with the results of the inspection. If part of EPC milestone, warranty claims or other technical due diligence, then adhereance with IEC 62446-3 is important. The levels to which an operator adheres to these will have a direct and significant bearing on service quality, cost and duration of the inspection task. Thermal camera resolution, lens type and flight height need to be recorded. For a typical array being flown with a 640x512 thermal camera with a 13mm lens, flying no higher than 23m above the module surface will achieve geometric resolution compliance. Deviations should be noted and justified. | - Documentation documenting camera resolution, lens and flight height. | 1 | 0%
C | Evaluation | 28 | Fully fulfilled | Partly fulfilled | Not fulfilled | 0
C.1 | Evaluation method | 6 |  |  |  | 0 | Evaluation method in compliance with IEC TS 62446-3: Looking for max. temperatures, temperature differences and temperature profiles and patterns. Documentation of irradiance, ambient temperature, cloud cover, wind speed and soiling level. Evaluation and classification of thermal abnormalities. Projection of temperature differences to nominal irradiance. Tick "fully fulfilled" if the Contractor strictly follows all the IEC TS 62446-3 evaluation criteria. Tick "partly fulfilled" if the Contractor does not strictly follow the IEC TS 62446-3 but still carries out a reliable and consistent evaluation that complies with the Client’s specific requirements. | - Description of Evaluation methodology utilized | 1 | 0%
C.2 | Geolocation | 6 |  |  |  | 0 | Manual or automated location of PV modules inspected. Layout recreation with precise geolocation down to individual module ID. | - Description of the geolocation procedure | 1 | 0%
C.3 | Statistics & Trends | 5 |  |  |  | 0 | Basic or advanced data treatment to describe the impact of failures in the PV plant, e.g. degradation trends, failure distribution by harm degree and by module manufacturer, power losses assessment etc. | - Description of Statistics & trends available in the deliverable | 1 | 0%
C.4 | Evaluation Personnel | 5 |  |  |  | 0 | The Contractor ensures that the personnel in charge of the evaluation and the analysis (including subcontractors, if applicable) has appropriate knowledge in electro thermography assured by a certification. A certificate according to ISO 9712 can serve as confirmation (as suggested by the IEC TS 62446-3 Annex B - Qualification of personnel), or equivalent such as ANSI/ASNT CP-105 and CP-189. In the case that personnel is not involved in report creation or data analysis, The Contractor ensures that a system is in place to ensure accuracy and consistency, such as the oversight of the data evaluation by a certified thermographer according to ISO 9712 or equivalent. Tick "fully fulfilled" if the evaluation personnel holds a level 2 certification according to ISO 9712 or equivalent. Tick "partly fulfilled" if the evaluation personnel holds a level 1 certification according to ISO 9712 or equivalent. Tick "Not fulfilled" is the evaluation personnel doesn’t hold any ISO 9712 or equivalent certification. | - Description of experience of personnell utilized for evaluations - Documentation showing the oversight of the data evaluation by a thermographer certified accoding to ISO9712 - Explanation of quality control systems in place for personell and automation systems - Identification of subcontractors utilized - if any - and methodologies to ensure consistency in detection when using subcontractors | 1 | 0%
C.5 | Evaluation Accuracy | 6 |  |  |  | 0 | A Quality Assurance program is in place to ensure accuracy and consistency of data | - Descriptions of Quality Assurance programs for the creation of reports | 1 | 0%
D | Inspection Report | 12 | Fully fulfilled | Partly fulfilled | Not fulfilled | 0
D.1 | Inspection Report Content | 6 |  |  |  | 0 | Inspection report content shall contain detailed inspection information, specified in IEC TS 62446-3. | - Sample report | 1 | 0%
D.2 | Maintenance support | 3 |  |  |  | 0 | Maintenance support: The provider is able to identify possible root causes and make recommendations for remedial actions to minimise yield losses based on the defect criticality. It can be seen as a list of recommendations that can be directly translated into preventive or corrective field operations. Tick "fully fulfilled" if the evaluation includes failure location (directly usable by technicians), root cause identification, yield losses estimation and maintenance recommendations. Tick "partly fulfilled" if the evaluation only provides failure location and classification. | - Sample report | 1 | 0%
D.3 | Online platform | 3 |  |  |  | 0 | Existence of an online platform or tool that allows to access and download reports. Tick "fully fulfilled" if the platform provides user friendly way of displaying the precise location of each failure found in the plant and if it allows the automatic creation of a report on-demand. Tick "partly fulfilled" if the platform only allows the automatic creation of a report. | - Description of the platform - Access to a demo account | 1 | 0%
E | Services Warranty | 3 | Fully fulfilled | Partly fulfilled | Not fulfilled | 0
E.1 | Services warranty | 3 |  |  |  | 0 | Deliverables are covered by a performance warranty appropriate for the scope of services provided | - Details of the provided warranty on workmanship | 1 | 0%
F | Insurance | 6 | Fully fulfilled | Partly fulfilled | Not fulfilled | 0
F.1 | Insurance requirements | 6 |  |  |  | 0 | Deliverables and inspection service are covered by insurance appropriate for the scope of services provided | - Details of the provided Insurance on operations | 1 | 0%