## User Manual
Solar Monitoring Best Practices Mark Checklist (2024 edition) - User Manual

## Monitoring Checklist
Solar Best Practices Mark Checklist - Monitoring Services (2024 edition)
Learn more about the Solar Best Practices Mark here: |  | Version 02.01.2023 |  |  |  |  | The Solar Best Practices Mark is powered and maintained by SolarPower Europe. www.solarpowereurope.org
www.solarbestpractices.com | [6 empty] | The requirements have been developed by SolarPower Europe's Lifecycle Quality workstream.
Contractor details |  |  | Contractor logo
Company name: | [Company name] |  | Insert your logo here |  |  |  | Maximum Score: | 100
Address: | [Address] | [5 empty] | Score needed for compliance: | 80
Website: | [Website] | [5 empty] | [Company name]'s score: | 0
Contact person: | [Contact person] | [5 empty] | [Company name]'s result:
E-Mail: | [E-Mail] | [5 empty] | [Company name] does not meet the eligibility criteria of the Solar Best Practices Mark
Phone: | [Phone]
# | Requirements title and description | Max Score | Self-evaluation |  |  | Your Score | Explanations | Documents for the technical dossier | Calculation (this is not invisible to users)
A | Company general information | 9 | Fully fulfilled | Partly fulfilled | Not fulfilled | 0 |  |  | Answer (3=fully, 2=party, 1=not fulfilled) | Value
A.1 | Structured and appropriate company organization | 2 |  |  |  | 0 | Please mark "Fully fulfilled" only if you can provide a detailed organisation chart and key job profiles. In particular, number of people (FTE) dedicated to software development, research analysis and to customer support shall be available. | Detailed organization chart of the company and if applicable organization of the Monitoring Solution business unit. | 1 | 0%
A.2 | Year of establishment of the company and year of commercialization of the monitoring system are made available, as well as main KPIs: number of customers, number of GW monitored, ..) | 2 |  |  |  | 0 | The company should demonstrate stability and good health: as such, the company should be able to provide information as: - year when the monitoring solution was first launched - first year of integration for a client - total number of paying customers - number of MW connected to the system Please mark "Fully Fulfilled" if the solution was launched more than 5 years ago, "Partially Fulfilled" if more than 2 years ago. "Fully Fulfilled" should also be selected only if a reference of a customer connected for more than 3 consecutive year can be provided. | References of relevant customers should be available, as well as number of customers, number of GWs, average size of portfolios, average size of plants, number of device monitored. Written satisfaction statement of a customer with more than 3 years track record using the monitoring system. | 1 | 0%
A.3 | Company financial balance of last 3 years is made available. Annual turnover specific to the monitoring solution exceeds its costs. | 1 |  |  |  | 0 | Please mark "Fully fulfilled" only if you can provide a detailed balance sheet of the company or the Group and the company has a positive net results for at least 3 consecutive years. Please mark "Partly fulfilled" only if you can provide it for at least the previous year, otherwise mark "Not fulfilled". | Balance sheets and P&L audited and well accounted are available | 1 | 0%
A.4 | The company demonstrates high knowledge of the PV industry (eg. Include experts with > 10 years experience on the field, including on site) | 2 |  |  |  | 0 | The monitoring system should be based on real expertise on Solar PV , both on site activity and as R&D advisory. Please mark "Fully fulfilled" only if the company was active on the PV domain before (at least 1 year) developing a monitoring solution, "Partially fulfilled" if PV expertise has started less than one year before the launch of the monitoring solution. | Please provide CV of employees involved in the monitoring solution that can demonstrate relevant experience in PV industry and possibly before the launch of the monitoring solution on the market. | 1 | 0%
A.5 | ISO compliance | 2 |  |  |  | 0 | The monitoring system company holds ISO 9001 Certifications only ("Partially Fulfilled") or ISO 9001 & ISO 14001 ("Fully fulfilled") | Copy of Valid Certificates | 1 | 0%
B | SLA, support and training | 16 | Fully fulfilled | Partly fulfilled | Not fulfilled | 0
B.1 | Yearly availability of the system is at least 99% over one year | 3 |  |  |  | 0 | Mark "Fully Fulfilled" in case availability over the past 3 years is demonstrated to be at least 99%. "Partially Fulfilled" should be selected for availability between 95 and 99% | Provide description of downtime tracking system and how this is communicated to customer. Provide a document with tracked downtime for the last 3 years. | 1 | 0%
B.2 | Support is provided over different timezones | 3 |  |  |  | 0 | Please mark "Fully fulfilled" only if you can provide support to clients in +/- 3h timezones from one of your bases. | Provide a detailed list of support people and main office location with available working hours. | 1 | 0%
B.3 | Constant upgrades and clear view on roadmap | 3 |  |  |  | 0 | The system upgrades are systematically deployed to all customer pool and changes impacting user experience are communicated within 1 week from implementation. Please mark "Fully fulfilled" if upgrades are deployed at not extra cost and customers are notified within 1 week. "Partly fulfilled" if customers are notified after 1 week and "Not fulfilled" if no upgrades are provided at all. | Provide a copy of upgrade communications sent to customers within last 2 years. | 1 | 0%
B.4 | Trainings for users and super users are organized | 3 |  |  |  | 0 | A training programme is proposed and customizable in function of O&M contractor business. Regular information sessions on new functionalities are organized. Please mark "Fully fulfilled" if initial training programme is provided "Partly fulfilled" if rehearsal trainings are provided | List of training documentation and manuals available as well as list of reharsal or upgrade training organized over the last 2 years. | 1 | 0%
E.15 | Application Architecture Datasheet | 1 |  |  |  | 0 | The monitoring tool provider should provide relevant implementation details regarding software architecture, hardware requirements and software and license dependencies. Description of cloud usage if applicable. | Software architecture and hardware requirements sheets. | 1 | 0%
E.15 | Feature and API Development Agreement | 1 |  |  |  | 0 | The monitoring tool provider should provide a general procedure and hourly rates/fees for feature or API development requests. | General offer for development work. | 1 | 0%
E.16 | IT Support Agreement | 2 |  |  |  | 0 | The monitoring tool provider should provide technical and end-user support during the lifecycle of the system. There should be an issue tracking system that tracks any issue or support request. Issue tracking system should provide a status tracking for the customer. Support scope document should provide the response times, the support scope, and support language. | IT support scope document | 1 | 0%
C | Data collection, integrity and cybersecurity | 15 | Fully fulfilled | Partly fulfilled | Not fulfilled | 0
C.1 | Hardware independence | 3 |  |  |  | 0 | Data can be collected from any type of device (inverter, data logger, sensors), brand and model. | List of compatible devices already sending data into the monitoring system (brand, model) and clear plan for integration of possible new hardware. | 1 | 0%
C.2 | High granularity data management capability | 3 |  |  |  | 0 | The MS can manage data from any size of plants and portfolios and can support any level of object granularity (portfolio, plant, subplant, inverter, string box, string, module, sensors). Any type of timestamp granularity can be managed | Provide description of data model and examples of: biggest plant (MW, number and type of devices monitored), smallest plant, biggest portfolio (both in MW and number of plants managed) | 1 | 0%
C.3 | Real time data processing capability | 3 |  |  |  | 0 | To be marked "Fully Fulfilled" if data are processed and shown in the monitoring system in less than 1 sec. "Partially Fulfilled" if processing time is less than 1 min. | Provide description of data flow architecture and crytical maximum delays for each data processing step | 1 | 0%
C.4 | Data ownership & availability | 3 |  |  |  | 0 | The ownership of the data stays with the asset. The monitoring system administrator user is provided easy access (export or data warehouse to all relevant historical data. The client can request a dump of all collected data in a readable format. Security of data should be ensured by taking frequent backups and using encryption and secure protocols. A detailed backup plan should be in place as well. Entire raw data are stored for the entire duration of the contract | Please provide information about your backup plan, password policies, encryption, protocols of communication and any relevant information. | 1 | 0%
C.5 | Cybersecurity | 3 |  |  |  | 0 | The monitoring system provider is responsible to guarantee data integrity and security. This include and not restrict to actively secure the servers accessing and transferring the data through the highest level of security measures available (Site to site VPN solutions should be the preferred setup) and insure redundancy of access to these servers (through backup and similar solutions)”. Principle of Cyber Hygene is to control the patch management of their end point connections. Also it is important to report and create every 6 months assessment test to check how users can be handling the Cyber Security Cyber Training for users, how oftern cybersecurity management is handled, this also includes phishing exercises. | Security risk assessment procedure is available. High level documentation should be provided and exchanged to show the details of the security measures used in any setup. Documentation from the Comms rooms, incluinding password management control (Basics diagram, IP range, documenation ) Patch Managemenet control, records on how ofter the sites get's updates. | 1 | 0%
D | Data analysis (Power Plant Operation) | 27 | Fully fulfilled | Partly fulfilled | Not fulfilled | 0
D.1 | Data aggregation | 3 |  |  |  | 0 | Data analysis should be performed on Plant, Portfolio and Account level. Dedicated analytical tools are available for in-depth data analysis of performance on plant level and lower. KPIs should be calculated as per the contract and exclusion periods should be taken into consideration for any KPI calculation, as per each individual contract. | Please provide a description on data analysis model, KPI calculation and aggregation. Simulation model for computed KPI shall be provided. | 1 | 0%
D.2 | Ability to measure and compute PV plant KPIs | 3 |  |  |  | 0 | The monitoring system user has the ability to manage, calculate and analyse PV plant KPIs such as PR and Yield, and to use the information to improve its perormance. Plant specific KPIs are normalized with units following the norm 61724 - Chapter 3. Please mark "Fully Fulfilled" if the monitoring system allows analysis of all following objects and "Partly Fulfilled" if only some of them: - portfolio - plant - inverter - junction box - string - sensor | Please provide a description on data analysis model, KPI calculation and aggregation. Simulation model for computed KPI shall be provided. | 1 | 0%
D.3 | Simulation model | 3 |  |  |  | 0 | The system include a simulation framework that models PV plants in line with industry practices. The expected behaviour of the PV plant under the actual meteorological conditions is simulated down to inverter and string level. "Digital twin" KPI's are provided for performances comparison and alerting. | Simulation framework description | 1 | 0%
D.4 | Irradiance & ambient meteo measurement management | 3 |  |  |  | 0 | The monitoring system should support - at least one solar irradiance measurement devices (partially fulfilled), ideally one for each module orientation plane (fully fullfilled) with resulting proper calculation of PR, expected yield, availability and any relevant KPI at inverter and plant level - at least one ambient temperature per plant - at least one module temperature sensors Every sensor should provide data with granularity max 15 minutes. | Please provide a description on data analysis model, KPI calculation and aggregation. Simulation model for computed KPI shall be provided. | 1 | 0%
D.5 | External independent meteo data & forecast references | 3 |  |  |  | 0 | Automated data collection of independent hourly meteo data (irradiation, ambient temperature, wind speed, snow coverage) should be provided through the monitoring interface from an independent meteo source that has been validated. Such enriched data are available at hourly granularity or less (15 minutes if possible). The data must be retrieved once per day at least. Solar irradiance data are also available from an independent source and power forecast is calculated using the same expected yield model as per historical data and based on the model. Irradiance data shall have a validated confidence interval of 5%. | Description of independent irradiation and meteo services provider (external service or included in the monitoring tool) including validation body certification. Where applicable, description of irradiation forecast provider and forecast expected yield model. | 1 | 0%
D.6 | Ability to track O&M contractor quality KPI's | 2 |  |  |  | 0 | The monitoring system user has the ability to manage KPIs strictly related to the O&M activities such as reaction time, resolution, energy lost between failure detection and resolution and to produce reports on top of it. | Example of monthly report with assessment of availability compared to contractual values and assessment of Unavailabilities at String or at Inverter level with related faults highlighted in the monitoring system. | 1 | 0%
D.7 | Proper use of exclusion factors | 2 |  |  |  | 0 | O&M and Power plant KPIs used for reporting purposes such as Availability and PR cn be calculated by excluding periods during which the power generation of the plant was reduced due to external (exclusion) factors. Exclusion factors shall be available at any device level and any time granulrity ("Fully Fulfilled"). | Description of exclusion factor model and list of KPI's being affected by the exclusion. | 1 | 0%
D.8 | Proper definition of the Minimum Irradiance Threshold (MIT) | 2 |  |  |  | 0 | The Minimum Irradiance Threshold (MIT) is defined according to site and plant characteristics (e.g. type of inverter, DC/AC ratio etc.) and can be defined in the monitoring system at least at inverter level by the monitoring user. This threshold is used for the computation of contractual and non contractual KPI's. | Description of the model where the MIT is taken into account for the computation of relevant KPI (PR, PR simulation, availability etc) | 1 | 0%
D.9 | Device replacement management | 2 |  |  |  | 0 | Replacement of devices are managed through the monitoring system such that analysis on predictive maintenance (eg preventive maintenance / device degradation /estimated wearing out of devices) can be computed counting on the real condition of equipment on site. | Description of device replacement management. | 1 | 0%
D.10 | Customisable analysis user interface | 2 |  |  |  | 0 | The user interface shall be adaptble on the fly to allow the user to compare all available indicators at all available object levels in time-dependent graphs, tables or scatter plots for in depth understanding of performances. Customized analysis can be saved for further use and for dashboarding | User manual of analysis configuration possibilities | 1 | 0%
D.11 | Ability to show MV status | 1 |  |  |  | 0 | The system should be able to show values and status of MV equipment, e.g. UPS, protection relay | User manual | 1 | 0%
D.12 | Ability to track tracker's KPI | 1 |  |  |  | 0 | In case when tracker systems are used, it is neccessary to know the angle and tilt (if two axcis). Possibility to use individual thresholds for alarming, e.g. deviation traget/actual angle | User manual | 1 | 0%
E | Functionalities | 33 | Fully fulfilled | Partly fulfilled | Not fulfilled | 0
E.1 | Flexible User Management | 2 |  |  |  | 0 | Access to the monitoring system sections, plants and data granularity shall selectable by the account administrator that has the possibility to create and customize as many user accessess as needed. | Description of the user management system and possible settings. | 1 | 0%
E.2 | Accessible plant configuration interface | 2 |  |  |  | 0 | The user has the possibility to configure the model of each asset through the user interface where the plant set up can be checked and adapted at any moment, for example for device replacement information. | User manual | 1 | 0%
E.3 | Easy dashboarding | 2 |  |  |  | 0 | Different options are provided to customize information overviews in order to optimize operational processes. User shall be able to set up personal dashboards including alarm lists, map overviews, customizable analysis of portfolio, plant and devices. Possibility to create customer dashboards with personalized information and secure access from external networks. | User manual of dashboarding funcionalities | 1 | 0%
E.4 | Configurable alarm management | 3 |  |  |  | 0 | The monitoring system allows the following alarms to be raised in the platform and sent by email: • Loss of communication • Plant stop • Inverter stop • Plant with Low Performance • Inverter with Low Performance (e.g. due to overheating) • String deviation All alarms are configurable in the monitorign system based on the knowledge of the solar asset The monitorign system administrator has the freedom to set up automatic notification (eg by email or SMS) to the users based on alarm severity. | Monitoring system documentation with list of available alarms and notification functionality description and description of alarma mangement procedures | 1 | 0%
E.5 | Document Management & Contract management | 2 |  |  |  | 0 | The monitoring system shall include an electronic Document Management System where documents are stored and backed up including versioning and history tracking of changes with timestamp and the respective user. User management shall be linked to access to document so that appropriate personel only has access to sensitive documentation. Various contractual parameters, and factors such as geographic location, project size, construction and offtaker arrangements shall be used for document archiving purposes. | Description of DMS including data based security description | 1 | 0%
E.6 | Ticketing management | 3 |  |  |  | 0 | Basics: The ticketing system allows to plan and record interventions (preventative, corrective or other) and includes at least essential details (Acknowledgment, response and resolution times, time of intervention, duration and outcome) as well as information about the actual activities conducted, equipment/devices affected, pictures, spare parts used. The tickets ca be generated starting from alerts and alarms generated automatically by the monitoring system. (Partially fullfilled) Interoperability: Every ticket shall be exportable alone or in bulk for reporting purposes. The monitoring system can import tickets details and document from an external ticketing system application ("Fully Fulfilled") | Complete description of ticketing system and ticket workflow. | 1 | 0%
E.7 | Annual management plan | 2 |  |  |  | 0 | An Annual Operations and Maintenance Plan is uploadable in the monitoring system at the beginning of the maintenance period and available for proper scheduling within an intervention calendar | Template or example of an annual operation management plan. | 1 | 0%
E.8 | Stock management | 3 |  |  |  | 0 | Spare parts management functionalities shall include: - warehouse management with incrementing /decrementing - parts location management - Spart parts inventory: Serial number, replacement register, …. | Description of stock management in the monitoring system | 1 | 0%
E.9 | Mobile application | 2 |  |  |  | 0 | A mobile application is available for monitoring of main plant and portfolio KPI's ("Partially Fulfilled" ) Tickets from site can be managed through the mobile application also when it runs on off-line mode. Documents such as pictures can be uploaded though the mobile application ("Fully Fulfilled"). | Description of mobile application functionalities, user management and data encryption description | 1 | 0%
E.10 | Advanced fault analysis / Machine learning functionalities | 3 |  |  |  | 0 | Artificial intelligence applications are available for advances analysis such as fault detection, irradiance data validation, performance assessment of each plant device. Please mark "Fully fulfilled" if a root-cause analysis is done and actionable maintenance actions are provided. Mark "Partly fulfilled " if only basic fault analysis is done (e.g. detection of underperformane without indicating possible causes). | POC with clear description and examples of advanced analysis available though the monitoring system | 1 | 0%
E.11 | Reporting | 3 |  |  |  | 0 | All data, raw and aggregated, including manual operations can be exported for automated report production. Report of intervention can be produced. Automatic reports can be uploaded in the monitoring system and being accessible to a restricted number of users based on their permissions. | sample reports and POC of data mining technology | 1 | 0%
E.12 | Interoperability Export API | 2 |  |  |  | 0 | The system can make available all relevant data (monitoring data, KPI's, asset characteristics, alarms and tasks, documents) through appropriate API's. Preferred format is REST as it supports xml, csv and json files; SOAP as an alternative though less flexible. | Api documentation | 1 | 0%
E.13 | Interoperability bidirectional API | 2 |  |  |  | 0 | The system allows to exchange information and synchronize with external platforms such as ticketing field management systems, ERP & CRM systems. Whereas these external systems provide bidirectional API 's, the monitoring system has the flexibility to develop specific interfacing modules to manage the synchronization. | API documentation | 1 | 0%
E.14 | Bulk export and import of data | 2 |  |  |  | 0 | All relevant data can be exported directly from the user interface upon manual request. The system can generate parc configuration from bulk documents (spreadsheet, csv files) uploaded through it's API or through its configuration tool. | Data export should be described in the user manual | 1 | 0%